## Asset Register
Sheet designed by PAT Testing Course: https://pattestingcourse.org.uk/
A–G · Persistent fields | [6 empty] | H–K · Last test summary |  |  |  | L–M · Status
A Asset ID | B Description | C Make/Model | D Class | E Type | F Location | G Date In Service | H Last Test Date | I Result | J Tester | K Next Test Date | L Status | M Notes
OFC-K001 | Kettle | Russell Hobbs 24711 | 1 | portable | Office Kitchen | 2024-03-15 | 2025-09-12 | Pass | J. Smith (C&G 2377-22) | 2027-09-12 | In Service | Cable strain relief showing minor wear — monitor
OFC-M002 | Microwave | Panasonic NN-E27JWMBPQ | 1 | movable | Office Kitchen | 2023-06-01 | 2025-09-12 | Pass | J. Smith (C&G 2377-22) | 2027-09-12 | In Service
OFC-L003 | Desk lamp | IKEA Forså | 2 | portable | Workstation 4 | 2022-01-20 | 2025-09-12 | Fail | J. Smith (C&G 2377-22) |  | Removed | Damaged flex; replaced 13/09/2025
WS-D012 | Drill charger | DeWalt DCB115 | 1 | portable | Workshop | 2024-07-10 | 2025-09-12 | Fail | J. Smith (C&G 2377-22) |  | Removed | Returned to manufacturer for assessment
WH-K005 | Microwave | Sharp R-22AT | 1 | movable | Warehouse Kitchen | 2013-04-08 | 2025-09-12 | Fail | J. Smith (C&G 2377-22) |  | Disposed | Beyond economic repair; replaced WH-K006

## Test History Log
Sheet designed by PAT Testing Course: https://pattestingcourse.org.uk/
A–F · Test context | [5 empty] | G–K · Test readings |  |  |  |  | L–M · Outcome
A Asset ID | B Test Date | C Tester | D Qualification | E PAT Tester Used | F Calibration Date | G Visual | H Earth (Ω) | I Insulation (MΩ) | J Polarity | K Functional | L Result | M Notes / Action
OFC-K001 | 2025-09-12 | J. Smith | C&G 2377-22 | Seaward Apollo 600 (S/N A6-12345) | 2025-03-15 | Pass | 0.08 | >299 | Pass | Pass | Pass | Cable strain relief showing minor wear — monitor
OFC-K001 | 2023-09-14 | M. Jones | C&G 2377-22 | Seaward Apollo 600 (S/N A6-12345) | 2023-02-22 | Pass | 0.06 | >299 | Pass | Pass | Pass
OFC-L003 | 2025-09-12 | J. Smith | C&G 2377-22 | Seaward Apollo 600 (S/N A6-12345) | 2025-03-15 | Fail | N/A | >299 | Pass | Fail | Fail | Damaged flex — remove from service; replace 13/09/2025

## Failed Items Log
Sheet designed by PAT Testing Course: https://pattestingcourse.org.uk/
A–F · Failure record | [5 empty] | G–J · Action |  |  |  | K–M · Resolution
A Asset ID | B Description | C Failure Date | D Failed By | E Failure Type | F Failure Details | G Action Required | H Action Taken | I Action Date | J Action By | K Replacement ID | L Status | M Notes
OFC-L003 | Desk lamp | 2025-09-12 | J. Smith | Visual / Functional | Damaged flex sheath at lamp head; intermittent cut-out | Replace | Replaced with new unit; old unit removed from service | 2025-09-13 | Office Mgr | OFC-L004 | Closed | Disposed via WEEE
WS-D012 | Drill charger | 2025-09-12 | J. Smith | Insulation Resistance | 0.4 MΩ — below 1 MΩ threshold | Investigate / Repair | Returned to manufacturer for assessment under warranty | 2025-09-16 | A. Patel |  | In Progress | Held in failed items store; tagged "Do Not Use"
WH-K005 | Microwave | 2025-09-12 | J. Smith | Earth Continuity | 1.2 Ω — well above 0.1 Ω limit; loose internal earth | Dispose | Beyond economic repair (12+ yrs); disposed via WEEE | 2025-09-14 | Facilities | WH-K006 | Closed | New unit added to register